## Modbus_var
Address |  | Reg. N° | Parameter | Description | Display Mode | Type | Unit | Value |  |  | Comment | Abbreviations for Type
hexadecimal | decimal | [6 empty] | Min. | Max. | Default
0x0001 | 1 | 1 | ALM_COOLER_FREEZE_F | Cooler Freeze Protection | 1bit BOOL | DI |  | 0 | 1 | 0 |  | CO | COILS_MEDIA
0x0005 | 5 | 1 | ALM_LOW_SUCTION_A_F | Circuit A Low Suction Temperature | 1bit BOOL | DI |  | 0 | 1 | 0 |  | IR | INPUT_REG_MEDIA
0x0006 | 6 | 1 | ALM_LOW_SUCTION_B_F | Circuit B Low Suction Temperature | 1bit BOOL | DI |  | 0 | 1 | 0 |  | DI | DISCR_INPUT_MEDIA
0x0008 | 8 | 1 | ALM_HIGH_SH_A_F | Circuit A High Superheat | 1bit BOOL | DI |  | 0 | 1 | 0 |  | HR | HOLDING_REG_MEDIA
0x0009 | 9 | 1 | ALM_HIGH_SH_B_F | Circuit B High Superheat | 1bit BOOL | DI |  | 0 | 1 | 0
0x000B | 11 | 1 | ALM_LOW_SH_A_F | Circuit A Low Superheat | 1bit BOOL | DI |  | 0 | 1 | 0
0x000C | 12 | 1 | ALM_LOW_SH_B_F | Circuit B Low Superheat | 1bit BOOL | DI |  | 0 | 1 | 0
0x000E | 14 | 1 | ALM_LOCK_F | Customer Interlock Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x001C | 28 | 1 | ALM_ELEC_BOX_F | Electrical Box Thermostat or Electrical Interlock failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x001E | 30 | 1 | ALM_LOSS_COM_MS_F | Master/Slave communication Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x001F | 31 | 1 | ALM_CCN_EMSTOP_F | Unit is in Network emergency stop | 1bit BOOL | DI |  | 0 | 1 | 0
0x0020 | 32 | 1 | ALM_COOL_PUMP1_F | Cooler pump #1 default | 1bit BOOL | DI |  | 0 | 1 | 0
0x0021 | 33 | 1 | ALM_COOL_PUMP2_F | Cooler pump #2 default | 1bit BOOL | DI |  | 0 | 1 | 0
0x0025 | 37 | 1 | ALM_SCT_OUT_OF_CP_M_A_F | Circ A - High condensing temperature out of map compressor | 1bit BOOL | DI |  | 0 | 1 | 0
0x0026 | 38 | 1 | ALM_SCT_OUT_OF_CP_M_B_F | Circ B - High condensing temperature out of map compressor | 1bit BOOL | DI |  | 0 | 1 | 0
0x0032 | 50 | 1 | ALM_REFRIG_ESCAPE_F | Refrigerant Leakage Detection | 1bit BOOL | DI |  | 0 | 1 | 0
0x0034 | 52 | 1 | ALM_HR_FLOW_SW_F | Heat Reclaim flow switch failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0043 | 67 | 1 | ALM_LOW_OIL_A_P_F | Circuit A Low Oil Pressure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0044 | 68 | 1 | ALM_LOW_OIL_B_P_F | Circuit B Low Oil Pressure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0046 | 70 | 1 | ALM_OIL_FILT_A_P_F | Circuit A Max Oil Filter Differential Pressure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0047 | 71 | 1 | ALM_OIL_FILT_B_P_F | Circuit B Max Oil Filter Differential Pressure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0049 | 73 | 1 | ALM_COND_PMP1_F | Condenser pump #1 default | 1bit BOOL | DI |  | 0 | 1 | 0
0x004A | 74 | 1 | ALM_COND_PMP2_F | Condenser pump #2 default | 1bit BOOL | DI |  | 0 | 1 | 0
0x004B | 75 | 1 | ALM_LOW_OIL_LEVEL_A_F | Circuit A Low Oil level | 1bit BOOL | DI |  | 0 | 1 | 0
0x004C | 76 | 1 | ALM_LOW_OIL_LEVEL_B_F | Circuit B Low Oil level | 1bit BOOL | DI |  | 0 | 1 | 0
0x004E | 78 | 1 | ALM_HIGH_DGT_A_F | Circuit A High Discharge Gas Temperature | 1bit BOOL | DI |  | 0 | 1 | 0
0x004F | 79 | 1 | ALM_HIGH_DGT_B_F | Circuit B High Discharge Gas Temperature | 1bit BOOL | DI |  | 0 | 1 | 0
0x0051 | 81 | 1 | ALM_SUCT_VALV_CLOSD_A_F | Circuit A Low economizer pressure or suction valve closed | 1bit BOOL | DI |  | 0 | 1 | 0
0x0052 | 82 | 1 | ALM_SUCT_VALV_CLOSD_B_F | Circuit B Low economizer pressure or suction valve closed | 1bit BOOL | DI |  | 0 | 1 | 0
0x0054 | 84 | 1 | ALM_OIL_DROP_A_P_F | Circuit A High Oil Filter Pressure Drop | 1bit BOOL | DI |  | 0 | 1 | 0
0x0055 | 85 | 1 | ALM_OIL_DROP_B_P_F | Circuit B High Oil Filter Pressure Drop | 1bit BOOL | DI |  | 0 | 1 | 0
0x005A | 90 | 1 | ALM_FLOW_CONFIG_F | Cooler Flow Switch Setpoint Configuration Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x005B | 91 | 1 | ALM_COOLER_FLOW_F | Cooler Flow Switch Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0061 | 97 | 1 | ALM_SENSORS_SWAP_F | Water Exchanger Temperature Sensors Swapped | 1bit BOOL | DI |  | 0 | 1 | 0
0x0065 | 101 | 1 | ALM_FC_PROCESS_F | DC Free Cooling Process Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x006A | 106 | 1 | ALM_SST_OUT_OF_CP_M_A_F | Circuit A - saturated suction Temperature out of MAP compressor | 1bit BOOL | DI |  | 0 | 1 | 0
0x006B | 107 | 1 | ALM_SST_OUT_OF_CP_M_B_F | Circuit B - saturated suction Temperature out of MAP compressor | 1bit BOOL | DI |  | 0 | 1 | 0
0x006E | 110 | 1 | ALM_LACK_OF_REF_A_F | Lack of refrigerant suspected on circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x006F | 111 | 1 | ALM_LACK_OF_REF_B_F | Lack of refrigerant suspected on circuit B | 1bit BOOL | DI |  | 0 | 1 | 0
0x0071 | 113 | 1 | ALM_DRV_CMP_LOW_F_A_F | Compressor frequency below min frequency threshold - Circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x0072 | 114 | 1 | ALM_DRV_CMP_LOW_F_B_F | Compressor frequency below min frequency threshold - Circuit B | 1bit BOOL | DI |  | 0 | 1 | 0
0x0074 | 116 | 1 | ALM_LOW_DSH_A_F | Discharge superheat too low - Circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x0075 | 117 | 1 | ALM_LOW_DSH_B_F | Discharge superheat too low - Circuit B | 1bit BOOL | DI |  | 0 | 1 | 0
0x0077 | 119 | 1 | ALM_OIL_VALV_A_F | Compressor oil valve default - circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x0078 | 120 | 1 | ALM_OIL_VALV_B_F | Compressor oil valve default - circuit B | 1bit BOOL | DI |  | 0 | 1 | 0
0x007A | 122 | 1 | ALM_DEMO_SW_PROT_F | Replacement Mode: please contact ERCD to activate options | 1bit BOOL | DI |  | 0 | 1 | 0
0x007B | 123 | 1 | ALM_CMP_CFG_A_F | Wrong compressor Type configuration circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x007C | 124 | 1 | ALM_CMP_CFG_B_F | Wrong compressor Type configuration circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x0080 | 128 | 1 | ALM_HR_COND_FREEZE_A_F | Heat Reclaim Condenser Freeze Protection - Circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x0081 | 129 | 1 | ALM_HR_COND_FREEZE_B_F | Heat Reclaim Condenser Freeze Protection - Circuit B | 1bit BOOL | DI |  | 0 | 1 | 0
0x03E9 | 1001 | 1 | ALM_HIGH_CP_TMP_A_F | Compressor A Motor temperature too high | 1bit BOOL | DI |  | 0 | 1 | 0
0x03EB | 1003 | 1 | ALM_HP_SWITCH_A_F | Compressor A High Pressure Switch protection | 1bit BOOL | DI |  | 0 | 1 | 0
0x0515 | 1301 | 1 | ALM_HIGH_CP_TMP_B_F | Compressor B Motor temperature too high | 1bit BOOL | DI |  | 0 | 1 | 0
0x0517 | 1303 | 1 | ALM_HP_SWITCH_B_F | Compressor B High Pressure Switch protection | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D1 | 2001 | 1 | ALM_DP_A_F | Circuit A Discharge Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D2 | 2002 | 1 | ALM_DP_B_F | Circuit B Discharge Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D4 | 2004 | 1 | ALM_SP_A_F | Circuit A Suction Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D5 | 2005 | 1 | ALM_SP_B_F | Circuit B Suction Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07DA | 2010 | 1 | ALM_OIL_P_A_F | Circuit A Oil Pressure Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07DB | 2011 | 1 | ALM_OIL_P_B_F | Circuit B Oil Pressure Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07DD | 2013 | 1 | ALM_ECO_P_A_F | Circuit A Economizer Pressure Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07DE | 2014 | 1 | ALM_ECO_P_B_F | Circuit B Economizer Pressure Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07E8 | 2024 | 1 | ALM_WATER_P_1_F | Water Pressure 1 transducer failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x07E9 | 2025 | 1 | ALM_WATER_P_2_F | Water Pressure 2 transducer failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x07ED | 2029 | 1 | ALM_WATER_P_TOO_LOW | Water Pressure too low - Pump cavitation risks | 1bit BOOL | DI |  | 0 | 1 | 0
0x07EF | 2031 | 1 | ALM_LIQUID_P_A_F | Circuit A Condenser Subcooling Liquid Pressure Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x07F0 | 2032 | 1 | ALM_LIQUID_P_B_F | Circuit B Condenser Subcooling Liquid Pressure Transducer | 1bit BOOL | DI |  | 0 | 1 | 0
0x0BB8 | 3000 | 1 | ALM_INI_FACT_CONF_F | No factory configuration | 1bit BOOL | DI |  | 0 | 1 | 0
0x0BB9 | 3001 | 1 | ALM_ILL_FACT_CONF_F | Illegal factory configuration Number #1 to nn | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C1C | 3100 | 1 | ALM_HK_OVER_FLOW_F | Cooler Water over flow in hydraulic kit | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C1D | 3101 | 1 | ALM_SERVICE_MAINT_ALERT | Service maintenance alert Number # nn | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C88 | 3208 | 1 | ALM_LOW_WL_PRESS_CROS_F | Cooler Water Loop : Pressure Sensors Crossed | 1bit BOOL | DI |  | 0 | 1 | 0
0x0CE5 | 3301 | 1 | ALM_M_S_CONFIG_F | Master chiller configuration error Number #1 to nn | 1bit BOOL | DI |  | 0 | 1 | 0
0x0DAC | 3500 | 1 | ALM_DATABASE_F | Database module Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0E10 | 3600 | 1 | ALM_LENSCAN_F | Lenscan module Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0FB4 | 4020 | 1 | ALM_STEPPER_EXV_A_F | Main EXV stepper motor Failure - cir A | 1bit BOOL | DI |  | 0 | 1 | 0
0x0FB5 | 4021 | 1 | ALM_STEPPER_EXV_B_F | Main EXV stepper motor Failure - cir B | 1bit BOOL | DI |  | 0 | 1 | 0
0x0FB7 | 4023 | 1 | ALM_STEPPER_ECO_A_F | EXV eco stepper motor Failure - cir A | 1bit BOOL | DI |  | 0 | 1 | 0
0x0FB8 | 4024 | 1 | ALM_STEPPER_ECO_B_F | EXV eco stepper motor Failure - cir B | 1bit BOOL | DI |  | 0 | 1 | 0
0x1195 | 4501 | 1 | ALM_FAN1_COM_F | Loss of communication with Aux Board Number 1 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1196 | 4502 | 1 | ALM_FAN2_COM_F | Loss of communication with Aux Board Number 2 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1197 | 4503 | 1 | ALM_FAN3_COM_F | Loss of communication with Aux Board Number 3 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1198 | 4504 | 1 | ALM_FAN4_COM_F | Loss of communication with Aux Board Number 4 | 1bit BOOL | DI |  | 0 | 1 | 0
0x11F9 | 4601 | 1 | ALM_FC_AUX1_COM_F | Loss of communication with DC Free Cooling Board | 1bit BOOL | DI |  | 0 | 1 | 0
0x11FB | 4603 | 1 | ALM_EMM_BRD_COM_F | Loss of communication with Energy Management Board | 1bit BOOL | DI |  | 0 | 1 | 0
0x11FC | 4604 | 1 | ALM_HR_BOARD_COM_F | Loss of communication with SIOB Board Heat Reclaim | 1bit BOOL | DI |  | 0 | 1 | 0
0x125D | 4701 | 1 | ALM_VLT_DRIVE1_COM_F | Loss of communication with Drive Board Number 1 | 1bit BOOL | DI |  | 0 | 1 | 0
0x125E | 4702 | 1 | ALM_VLT_DRIVE2_COM_F | Loss of communication with Drive Board Number 2 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1260 | 4704 | 1 | ALM_FAN_DRIVEA1_COM_F | Loss of communication with Drive Board Number 4 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1261 | 4705 | 1 | ALM_FAN_DRIVEA2_COM_F | Loss of communication with Drive Board Number 5 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1262 | 4706 | 1 | ALM_FAN_DRIVEA3_COM_F | Loss of communication with Drive Board Number 6 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1263 | 4707 | 1 | ALM_FAN_DRIVEB1_COM_F | Loss of communication with Drive Board Number 7 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1264 | 4708 | 1 | ALM_FAN_DRIVEB2_COM_F | Loss of communication with Drive Board Number 8 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1265 | 4709 | 1 | ALM_FAN_DRIVEB3_COM_F | Loss of communication with Drive Board Number 9 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1266 | 4710 | 1 | ALM_PUMP_DRIVE_1_COM_F | Loss of communication with VFD Pump Drive Board Number 1 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1267 | 4711 | 1 | ALM_PUMP_DRIVE_2_COM_F | Loss of communication with VFD Pump Drive Board Number 2 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1325 | 4901 | 1 | ALM_SIOB1_COM_F | Loss of communication with SIOB Board Number 1 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1326 | 4902 | 1 | ALM_SIOB2_COM_F | Loss of communication with SIOB Board Number 2 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1389 | 5001 | 1 | ALM_COOL_EWT_F | Cooler Entering Fluid Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x138A | 5002 | 1 | ALM_COOL_LWT_F | Cooler Leaving Fluid Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1390 | 5008 | 1 | ALM_HR_EWT_F | Reclaim Condenser Entering Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1391 | 5009 | 1 | ALM_HR_LWT_F | Reclaim Condenser Leaving Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1392 | 5010 | 1 | ALM_OAT_F | OAT Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1393 | 5011 | 1 | ALM_CHWSTEMP_F | MASTER/Slave Common Fluid Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1394 | 5012 | 1 | ALM_SUCTION_T_A_F | Circuit A Suction Gas Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1395 | 5013 | 1 | ALM_SUCTION_T_B_F | Circuit B Suction Gas Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1397 | 5015 | 1 | ALM_DGT_A_T_F | Circuit A Discharge Gas Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x1398 | 5016 | 1 | ALM_DGT_B_T_F | Circuit B Discharge Gas Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x139A | 5018 | 1 | ALM_LIQUID_T_A_F | Circuit A Condenser Subcooling Liquid Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x139B | 5019 | 1 | ALM_LIQUID_T_B_F | Circuit B Condenser Subcooling Liquid Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x139D | 5021 | 1 | ALM_SPACE_TEMP_F | Space Temperature Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x139F | 5023 | 1 | ALM_COOL_HEAT_T_F | Cooler heater feedback thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x13A0 | 5024 | 1 | ALM_ECO_T_A_F | Circuit A Economizer Gas Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13A1 | 5025 | 1 | ALM_ECO_T_B_F | Circuit B Economizer Gas Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13A9 | 5033 | 1 | ALM_CP_TMP_A_F | Circuit A compressor Motor Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x13AA | 5034 | 1 | ALM_CP_TMP_B_F | Circuit B compressor Motor Thermistor | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B6 | 5046 | 1 | ALM_FC_WLOOP_F | DC Free Cooling Water Loop Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B7 | 5047 | 1 | ALM_FC_LWT_F | DC Free Cooling Leaving Water Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B8 | 5048 | 1 | ALM_FC_OAT_F | DC Free Cooling OAT Sensor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1771 | 6001 | 1 | ALM_VLT_DRIVE_A_F | Circuit A Compressor VFD Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x17D5 | 6101 | 1 | ALM_VLT_DRIVE_B_F | Circuit B Compressor VFD Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x189D | 6301 | 1 | ALM_FAN_DRIVE_A1_F | Circuit A Fan VFD 1 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1901 | 6401 | 1 | ALM_FAN_DRIVE_A2_F | Circuit A Fan VFD 2 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1965 | 6501 | 1 | ALM_FAN_DRIVE_A3_F | Circuit A Fan VFD 3 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x19C9 | 6601 | 1 | ALM_FAN_DRIVE_B1_F | Circuit B Fan VFD 1 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1A2D | 6701 | 1 | ALM_FAN_DRIVE_B2_F | Circuit B Fan VFD 2 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1A91 | 6801 | 1 | ALM_FAN_DRIVE_B3_F | Circuit B Fan VFD 3 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1AF5 | 6901 | 1 | ALM_PUMP_DRIVE_1_F | Hydronic kit pump 1 VFD Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1B59 | 7001 | 1 | ALM_PUMP_DRIVE_2_F | Hydronic kit pump 2 VFD Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1FA5 | 8101 | 1 | ALM_VLT_DRIVE_A_ALERT | Circuit A Compressor VFD Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x2009 | 8201 | 1 | ALM_VLT_DRIVE_B_ALERT | Circuit B Compressor VFD Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x20D1 | 8401 | 1 | ALM_FAN_DRIVE_A1_ALERT | Circuit A Fan VFD 1 Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x2135 | 8501 | 1 | ALM_FAN_DRIVE_A2_ALERT | Circuit A Fan VFD 2 Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x2199 | 8601 | 1 | ALM_FAN_DRIVE_A3_ALERT | Circuit A Fan VFD 3 Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x21FD | 8701 | 1 | ALM_FAN_DRIVE_B1_ALERT | Circuit B Fan VFD 1 Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x2261 | 8801 | 1 | ALM_FAN_DRIVE_B2_ALERT | Circuit B Fan VFD 2 Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x22C5 | 8901 | 1 | ALM_FAN_DRIVE_B3_ALERT | Circuit B Fan VFD 3 Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x2329 | 9001 | 1 | ALM_PUMP_DRIVE_1_ALERT | Hydronic kit pump 1 VFD Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x238D | 9101 | 1 | ALM_PUMP_DRIVE_2_ALERT | Hydronic kit pump 2 VFD Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x0384 | 900 | 2 | SETPOINT_csp1 | Cooling Setpoint 1 | 32bits FLOAT | HR | °F | -20 | 78.8 | 44
[7 empty] | °C | -28.8889 | 26 | 6.6667
0x0386 | 902 | 2 | SETPOINT_csp2 | Cooling Setpoint 2 | 32bits FLOAT | HR | °F | -20 | 78.8 | 44
[7 empty] | °C | -28.8889 | 26 | 6.6667
0x0388 | 904 | 2 | SETPOINT_ice_sp | Cooling Ice Setpoint | 32bits FLOAT | HR | °F | -20 | 78.8 | 44
[7 empty] | °C | -28.8889 | 26 | 6.6667
0x038A | 906 | 2 | SETPOINT_hsp1 | Heating Setpoint 1 | 32bits FLOAT | HR | °F | 80 | 145.4 | 100
[7 empty] | °C | 26.6667 | 63 | 37.7778
0x038C | 908 | 2 | SETPOINT_hsp2 | Heating Setpoint 2 | 32bits FLOAT | HR | °F | 80 | 145.4 | 100
[7 empty] | °C | 26.6667 | 63 | 37.7778
0x038E | 910 | 2 | SETPOINT_lim_sp1 | Switch Limit Setpoint 1 | 32bits UINT | HR | PERCENT | 0 | 100 | 100
0x0390 | 912 | 2 | SETPOINT_lim_sp2 | Switch Limit Setpoint 2 | 32bits UINT | HR | PERCENT | 0 | 100 | 100
0x0392 | 914 | 2 | SETPOINT_lim_sp3 | Switch Limit Setpoint 3 | 32bits UINT | HR | PERCENT | 0 | 100 | 100
0x0BC2 | 3010 | 2 | PROTOCOL_CTRL_PNT | Control Point | 32bits FLOAT | HR | °F | -4 | 153 | 44.6
[7 empty] | °C | -20 | 67.2222 | 7
0x0BC6 | 3014 | 2 | PROTOCOL_DEM_LIM | Demand Limit | 32bits UINT | HR | PERCENT | 0 | 100 | 0
0x0BCE | 3022 | 2 | PROTOCOL_CHIL_S_S | Chiller Start/Stop | 32bits UINT | HR |  | 0 | 1 | 0
0x0BD0 | 3024 | 2 | PROTOCOL_EMSTOP | Emergency Stop | 32bits UINT | HR |  | 0 | 1 | 0
0x0BE4 | 3044 | 2 | PROTOCOL_HC_SEL | Heatcool Select | 32bits UINT | HR |  | 0 | 2 | 0
0x0BE6 | 3046 | 2 | PROTOCOL_SP_SEL | Setpoint Select | 32bits UINT | HR |  | 0 | 2 | 0
0x0C1A | 3098 | 2 | PROTOCOL_CPUMP_1 | Evaporator pump 1 | 32bits UINT | HR |  | 0 | 1 | 0
0x0C1C | 3100 | 2 | PROTOCOL_CPUMP_2 | Evaporator pump 2 | 32bits UINT | HR |  | 0 | 1 | 0
0x0C2A | 3114 | 2 | PROTOCOL_CHIL_OCC | Chiller occupied? | 32bits UINT | HR |  | 0 | 1 | 0
0x0C2C | 3116 | 2 | PROTOCOL_SP_OCC | Setpoint Occupied? | 32bits UINT | HR |  | 0 | 1 | 0
0x0FA0 | 4000 | 2 | MODBUSRS_metric | Metric Unit | 32bits UINT | HR |  | 0 | 1 | 1
0x0FA2 | 4002 | 2 | MODBUSRS_real_typ | Real type management | 32bits UINT | HR |  | 0 | 1 | 1
0x0FA4 | 4004 | 2 | MODBUSRS_swap_b | Swap Bytes | 32bits UINT | HR |  | 0 | 1 | 0
0x0FA6 | 4006 | 2 | MODBUSIP_metric | Metric Unit | 32bits UINT | HR |  | 0 | 1 | 1
0x0FA8 | 4008 | 2 | MODBUSIP_real_typ | Real type management | 32bits UINT | HR |  | 0 | 1 | 1
0x0FAA | 4010 | 2 | MODBUSIP_swap_b | Swap Bytes | 32bits UINT | HR |  | 0 | 1 | 0
0x1004 | 4100 | 2 | GENCONF_ice_cnfg | Ice Mode Enable | 32bits UINT | HR |  | 0 | 1 | 0
0x1006 | 4102 | 2 | GENCONF_lim_sel | Demand Limit Type Select | 32bits UINT | HR |  | 0 | 2 | 0
0x1008 | 4104 | 2 | GENCONF_ln_end | Low Noise End Hour | 32bits UINT | HR |  |  |  | 0
0x100A | 4106 | 2 | GENCONF_ln_limit | Low Noise Fan freq limit | 32bits FLOAT | HR | PERCENT | 60 | 100 | 75
0x100C | 4108 | 2 | GENCONF_ln_start | Low Noise Start Hour | 32bits UINT | HR |  |  |  | 0
0x100E | 4110 | 2 | GENCONF_nh_end | Night Mode End Hour | 32bits UINT | HR |  |  |  | 0
0x1010 | 4112 | 2 | GENCONF_nh_limit | Night Capacity Limit | 32bits UINT | HR | PERCENT | 0 | 100 | 100
0x1012 | 4114 | 2 | GENCONF_nh_start | Night Mode Start Hour | 32bits UINT | HR |  |  |  | 0
0x1014 | 4116 | 2 | GENCONF_off_on_d | Unit Off to On Delay | 32bits UINT | HR | MINUTES | 1 | 15 | 1
0x1016 | 4118 | 2 | GENCONF_pow_max | Maximum Power Limit | 32bits FLOAT | HR | KW | 0 | 2000 | 2000
0x1018 | 4120 | 2 | GENCONF_pow_sel | Power Limit select | 32bits UINT | HR |  | 0 | 1 | 0
0x101A | 4122 | 2 | GENCONF_prio_cir | Cir Priority Sequence | 32bits UINT | HR |  | 0 | 2 | 0
0x101C | 4124 | 2 | GENCONF_ramp_sel | Ramp Loading Select | 32bits UINT | HR |  | 0 | 1 | 0
0x101E | 4126 | 2 | GENCONF_seq_typ | Staged Loading Sequence | 32bits UINT | HR |  | 0 | 1 | 0
0x1020 | 4128 | 2 | GENCONF_shortcyc | short cycle management | 32bits UINT | HR |  | 0 | 1 | 0
0x1022 | 4130 | 2 | GENCONF_transcap | Cap. to start 2nd cir | 32bits UINT | HR | PERCENT | 30 | 80 | 50
0x1068 | 4200 | 2 | RESETCFG_cr_deg | Cooling Reset Deg. Value | 32bits FLOAT | HR | ^F | -30 | 30 | 0
[7 empty] | ^C | -16.6667 | 16.6667 | 0
0x106A | 4202 | 2 | RESETCFG_cr_sel | Cooling Reset Select | 32bits UINT | HR |  | 0 | 4 | 0
0x106C | 4204 | 2 | RESETCFG_dt_cr_fu | Delta T Full Reset Value | 32bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x106E | 4206 | 2 | RESETCFG_dt_cr_no | Delta T No Reset Value | 32bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x1070 | 4208 | 2 | RESETCFG_dt_hr_fu | Delta T Full Reset Value | 32bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x1072 | 4210 | 2 | RESETCFG_dt_hr_no | Delta T No Reset Value | 32bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x1074 | 4212 | 2 | RESETCFG_hr_deg | Heating Reset Deg. Value | 32bits FLOAT | HR | ^F | -30 | 30 | 0
[7 empty] | ^C | -16.6667 | 16.6667 | 0
0x1076 | 4214 | 2 | RESETCFG_hr_sel | Heating Reset Select | 32bits UINT | HR |  | 0 | 4 | 0
0x1078 | 4216 | 2 | RESETCFG_oat_crfu | OAT Full Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x107A | 4218 | 2 | RESETCFG_oat_crno | OAT No Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x107C | 4220 | 2 | RESETCFG_oat_hrfu | OAT Full Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x107E | 4222 | 2 | RESETCFG_oat_hrno | OAT No Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x1080 | 4224 | 2 | RESETCFG_spacr_fu | Space T Full Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x1082 | 4226 | 2 | RESETCFG_spacr_no | Space T No Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x1084 | 4228 | 2 | RESETCFG_spahr_fu | Space T Full Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x1086 | 4230 | 2 | RESETCFG_spahr_no | Space T No Reset Value | 32bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x1088 | 4232 | 2 | RESETCFG_v_cr_fu | Current Full Reset Value | 32bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x108A | 4234 | 2 | RESETCFG_v_cr_no | Current No Reset Value | 32bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x108C | 4236 | 2 | RESETCFG_v_hr_fu | Current Full Reset Value | 32bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x108E | 4238 | 2 | RESETCFG_v_hr_no | Current No Reset Value | 32bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x10CC | 4300 | 2 | PUMPCONF_cpumpseq | Cooler Pumps Sequence | 32bits UINT | HR |  | 0 | 4 | 0
0x10CE | 4302 | 2 | PUMPCONF_pump_del | Pump Auto Rotation Delay | 32bits UINT | HR | HOURS | 24 | 3000 | 48
0x10D0 | 4304 | 2 | PUMPCONF_pump_loc | Flow Checked If Pump Off | 32bits UINT | HR |  | 0 | 1 | 1
0x10D2 | 4306 | 2 | PUMPCONF_pump_per | Pump Sticking Protection | 32bits UINT | HR |  | 0 | 1 | 0
0x10D4 | 4308 | 2 | PUMPCONF_pump_sby | Stop Pump During Standby | 32bits UINT | HR |  | 0 | 1 | 0
0x10D6 | 4310 | 2 | PUMPCONF_stopcool | Cond Pump Off In Cool | 32bits UINT | HR |  | 0 | 1 | 0
0x10D8 | 4312 | 2 | PUMPCONF_stopheat | Cooler Pump Off In Heat | 32bits UINT | HR |  | 0 | 1 | 0
0x10DA | 4314 | 2 | SETPOINT_cramp_sp | Cooling Ramp Loading | 32bits FLOAT | HR | ^F | 0.2 | 20 | 1
[7 empty] | ^C | 0.11111 | 11.1111 | 0.55556
0x10DC | 4316 | 2 | SETPOINT_hramp_sp | Heating Ramp Loading | 32bits FLOAT | HR | ^F | 0.2 | 20 | 1
[7 empty] | ^C | 0.11111 | 11.1111 | 0.55556
0x10DE | 4318 | 2 | SETPOINT_cauto_sp | Cool Changeover Setpt | 32bits FLOAT | HR | °F | 39 | 122 | 75
[7 empty] | °C | 3.8889 | 50 | 23.8889
0x10E0 | 4320 | 2 | SETPOINT_hauto_sp | Heat Changeover Setpt | 32bits FLOAT | HR | °F | 32 | 115 | 64
[7 empty] | °C | 1.2e-06 | 46.1111 | 17.7778
0x10E2 | 4322 | 2 | SETPOINT_vpmpdtsp | Varipump Delta Temp Stp | 32bits FLOAT | HR | ^F | 1.8 | 36 | 9
[7 empty] | ^C | 1 | 20 | 5
0x10E4 | 4324 | 2 | SETPOINT_vpmpdpsp | Varipump Pressure Stp | 32bits FLOAT | HR | PSIG | 7.25 | 90 | 29
[7 empty] | kPa | 49.9887 | 620.55 | 199.955
0x23D2 | 9170 | 2 | PROTOCOL_RECL_SEL | Reclaim Select | 32bits UINT | HR |  | 0 | 1 | 0
0x23D4 | 9172 | 2 | PROTOCOL_ROTCPUMP | Rotate Cooler Pumps ? | 32bits UINT | HR |  | 0 | 1 | 0
0x23D6 | 9174 | 2 | HR_CFG_hr_cir | HR circuit selection | 32bits UINT | HR |  | 0 | 2 | 2
0x23D8 | 9176 | 2 | HR_CFG_hr_flui | HR condenser fluid | 32bits UINT | HR |  | 0 | 1 | 0
0x23DA | 9178 | 2 | HR_CFG_hr_eco | HR eco mode | 32bits UINT | HR |  | 0 | 1 | 0
0x23DC | 9180 | 2 | HR_CFG_rev_3WV | HR reverse 3WV cmd ? | 32bits UINT | HR |  | 0 | 1 | 0
0x23DE | 9182 | 2 | HR_CFG_HRewtctl | HR Control on EWT | 32bits UINT | HR |  | 0 | 1 | 0
0x23E0 | 9184 | 2 | HR_CFG_pg_HR3wv | Prop PID gain HR 3w valv | 32bits FLOAT | HR |  | -20 | 20 | 2
0x23E2 | 9186 | 2 | HR_CFG_ig_HR3wv | Int PID gain HR 3w valve | 32bits FLOAT | HR |  | -5 | 5 | 0.2
0x23E4 | 9188 | 2 | HR_CFG_dg_HR3wv | Deri PID gain HR 3w valv | 32bits FLOAT | HR |  | -20 | 20 | 0.4
0x23E6 | 9190 | 2 | GENCONF_minHR3wv | HR 3w valve min position | 32bits FLOAT | HR | PERCENT | 0 | 100 | 20
0x23E8 | 9192 | 2 | GENCONF_maxHR3wv | HR 3w valve max position | 32bits FLOAT | HR | PERCENT | 0 | 100 | 80
0x23EA | 9194 | 2 | SETPOINT_rsp | Heat Reclaim Setpoint | 32bits FLOAT | HR | °F | 68 | 149 | 122
[7 empty] | °C | 20 | 65 | 50
0x0000 | 0 | 2 | TEMP_EWT | Cooler Entering Fluid | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0002 | 2 | 2 | TEMP_LWT | Cooler Leaving Fluid | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0004 | 4 | 2 | TEMP_OAT | Outdoor Air Temperature | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0006 | 6 | 2 | CAPACTRL_ctrl_wt | Controled Water Temp | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0008 | 8 | 2 | TEMP_CHWSTEMP | CHWS Temperature | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x000A | 10 | 2 | GENUNIT_CTRL_PNT | Control Point | 32bits FLOAT | IR | °F | -4 | 153 | 0
[7 empty] | °C | -20 | 67.2222 | -17.7778
0x000C | 12 | 2 | GENUNIT_SP | Current Setpoint | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x000E | 14 | 2 | GENUNIT_DEM_LIM | Active Demand Limit Val | 32bits UINT | IR | PERCENT | 0 | 100 | 0
0x0010 | 16 | 2 | GENUNIT_CAP_T | Percent Total Capacity | 32bits UINT | IR | PERCENT |  |  | 0
0x0012 | 18 | 2 | GENUNIT_TOT_CURR | Actual Chiller Current | 32bits FLOAT | IR | AMPS |  |  | 0
0x0014 | 20 | 2 | GENUNIT_min_left | Minutes Left for Start | 32bits FLOAT | IR | MINUTES |  |  | 0
0x0016 | 22 | 2 | GENUNIT_CHIL_S_S | Net.: Cmd Start/Stop | 32bits UINT | IR |  | 0 | 1 | 0
0x0018 | 24 | 2 | GENUNIT_EMSTOP | Emergency Stop | 32bits UINT | IR |  | 0 | 1 | 0
0x001A | 26 | 2 | INPUTS_REM_LOCK | Customer Interlock | 32bits UINT | IR |  | 0 | 1 | 0
0x001C | 28 | 2 | OUTPUTS_RUNNING | Running Relay Status | 32bits UINT | IR |  | 0 | 1 | 0
0x001E | 30 | 2 | INPUTS_ONOFF_SW | Remote On/Off Switch | 32bits UINT | IR |  | 0 | 1 | 0
0x0022 | 34 | 2 | INPUTS_LIM_SW1 | Limit Switch 1 | 32bits UINT | IR |  | 0 | 1 | 0
0x0024 | 36 | 2 | INPUTS_LIM_SW2 | Limit Switch 2 | 32bits UINT | IR |  | 0 | 1 | 0
0x0026 | 38 | 2 | INPUTS_ICE_SW | Ice Done Storage Switch | 32bits UINT | IR |  | 0 | 1 | 0
0x0028 | 40 | 2 | GENUNIT_CTRL_TYP | Local=0 Net.=1 Remote=2 | 32bits UINT | IR |  | 0 | 3 | 0
0x002A | 42 | 2 | UNIT_STATUS | Run Status | 32bits UINT | IR |  |  |  | 0
0x002C | 44 | 2 | GENUNIT_HC_SEL | Heat/Cool Select | 32bits UINT | IR |  | 0 | 2 | 0
0x002E | 46 | 2 | GENUNIT_SP_SEL | Setpoint Select | 32bits UINT | IR |  | 0 | 2 | 0
0x003E | 62 | 2 | TEMP_T_HEATER | Cooler Heater Temp | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0048 | 72 | 2 | PRESSURE_EWATPRES | Entering water pressure | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x004A | 74 | 2 | PRESSURE_LWATPRES | Leaving water pressure | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x0054 | 84 | 2 | INPUTS_ELEC_BOX | Electrical box Interlock | 32bits UINT | IR |  | 0 | 1 | 0
0x0056 | 86 | 2 | OUTPUTS_READY | Ready or Running Status | 32bits UINT | IR |  | 0 | 1 | 0
0x005A | 90 | 2 | INPUTS_RECL_SW | Remote Reclaim switch | 32bits UINT | IR |  | 0 | 1 | 0
0x005E | 94 | 2 | INPUTS_SETP_SW | Remote Setpoint Switch | 32bits UINT | IR |  | 0 | 1 | 0
0x0062 | 98 | 2 | PUMPSTAT_CPUMP_1 | Cooler Pump #1 Command | 32bits UINT | IR |  | 0 | 1 | 0
0x0064 | 100 | 2 | PUMPSTAT_CPUMP_2 | Cooler Pump #2 Command | 32bits UINT | IR |  | 0 | 1 | 0
0x0066 | 102 | 2 | PUMPSTAT_FLOW_SW | Cooler Flow Switch | 32bits UINT | IR |  | 0 | 1 | 0
0x0070 | 112 | 2 | OUTPUTS_C_HEATER | Cooler Heater Output | 32bits UINT | IR |  | 0 | 1 | 0
0x0072 | 114 | 2 | GENUNIT_CHIL_OCC | Net.: Cmd Occupied | 32bits UINT | IR |  | 0 | 1 | 0
0x0074 | 116 | 2 | GENUNIT_SP_OCC | Setpoint Occupied? | 32bits UINT | IR |  | 0 | 1 | 1
0x0076 | 118 | 2 | BACnet_bacena | BACnet Enable | 32bits UINT | IR |  | 0 | 1 | 0
0x0078 | 120 | 2 | BACnet_bacunit | Metric Units? | 32bits UINT | IR |  | 0 | 1 | 1
0x007A | 122 | 2 | BACnet_network | Network | 32bits UINT | IR |  | 1 | 40000 | 1600
0x007C | 124 | 2 | BACnet_ident | Device Id Actually Used | 32bits FLOAT | IR |  | 1 | 4194302 | 1
0x007E | 126 | 2 | BACnet_COLOR | ALC color value | 32bits UINT | IR |  | 0 | 14 | 14
0x0080 | 128 | 2 | BACnet_PRIME_V | ALC prime value | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0082 | 130 | 2 | BACnet_BMS_OCC | BMS's request for occupancy: 0=UNOCC, 1=OCC, 2, None. | 32bits INT | IR |  | 0 | 2 | 2
0x0088 | 136 | 2 | OUTPUTS_WTANK_HT | Water Tank Heater | 32bits UINT | IR |  | 0 | 1 | 0
0x008A | 138 | 2 | PUMPSTAT_VPMP_CMD | Variable speed pump cmd | 32bits UINT | IR | PERCENT | 0 | 100 | 0
0x008C | 140 | 2 | PUMPSTAT_WAT_FLOW | Water flow (kit hydro) | 32bits FLOAT | IR | GPS |  |  | 0
[7 empty] | l/s |  |  | 0
0x008E | 142 | 2 | FACTORY_kithydro | Kit Hydro option | 32bits UINT | IR |  | 0 | 2 | 0
0x0092 | 146 | 2 | BACnet_sch_occ | BACnet schedule occupancy | 32bits UINT | IR |  | 0 | 1 | 0
0x03E8 | 1000 | 2 | RUNTIME_HR_MACH | Machine Operating Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x03EA | 1002 | 2 | RUNTIME_st_mach | Machine Starts Number | 32bits FLOAT | IR |  |  |  | 0
0x03EC | 1004 | 2 | RUNTIME_hr_cpum1 | Cooler Pump #1 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x03EE | 1006 | 2 | RUNTIME_hr_cpum2 | Cooler Pump #2 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x03F4 | 1012 | 2 | HR_PARTIAL_DOWNTIME | Cumulated Downtime when alarm state is partial | 32bits FLOAT | IR |  |  |  | 0
0x03F6 | 1014 | 2 | HR_TOTAL_DOWNTIME | Cumulated Downtime when alarm state is tripout | 32bits FLOAT | IR |  |  |  | 0
0x044C | 1100 | 2 | ALARMRST_alarm_1c | Current Alarm 1 | 32bits UINT | IR |  |  |  | 0
0x044E | 1102 | 2 | ALARMRST_alarm_2c | Current Alarm 2 | 32bits UINT | IR |  |  |  | 0
0x0450 | 1104 | 2 | ALARMRST_alarm_3c | Current Alarm 3 | 32bits UINT | IR |  |  |  | 0
0x0452 | 1106 | 2 | ALARMRST_alarm_4c | Current Alarm 4 | 32bits UINT | IR |  |  |  | 0
0x0454 | 1108 | 2 | ALARMRST_alarm_5c | Current Alarm 5 | 32bits UINT | IR |  |  |  | 0
0x0456 | 1110 | 2 | ALARMRST_alarm_1 | Jbus Current Alarm 1 | 32bits UINT | IR |  |  |  | 0
0x0458 | 1112 | 2 | ALARMRST_alarm_2 | Jbus Current Alarm 2 | 32bits UINT | IR |  |  |  | 0
0x045A | 1114 | 2 | ALARMRST_alarm_3 | Jbus Current Alarm 3 | 32bits UINT | IR |  |  |  | 0
0x045C | 1116 | 2 | ALARMRST_alarm_4 | Jbus Current Alarm 4 | 32bits UINT | IR |  |  |  | 0
0x045E | 1118 | 2 | ALARMRST_alarm_5 | Jbus Current Alarm 5 | 32bits UINT | IR |  |  |  | 0
0x0460 | 1120 | 2 | UNIT_ALM | Alarm Status | 32bits UINT | IR |  |  |  | 0
0x0462 | 1122 | 2 | OUTPUTS_ALARM | Alarm Relay Status | 32bits UINT | IR |  | 0 | 1 | 0
0x0464 | 1124 | 2 | OUTPUTS_ALERT | Alert Relay State | 32bits UINT | IR |  | 0 | 1 | 0
0x04B0 | 1200 | 2 | PRESSURE_DP_A | Discharge Pressure A | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x04B2 | 1202 | 2 | PRESSURE_SP_A | Main Suction Pressure A | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x04B4 | 1204 | 2 | PRESSURE_ECO_P_A | Economizer Pressure A | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x04B6 | 1206 | 2 | PRESSURE_OP_A | Oil Pressure A | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x04B8 | 1208 | 2 | PRESSURE_DOP_A | Oil Pressure DifferenceA | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x04BA | 1210 | 2 | TEMP_SCT_A | Saturated Cond Tmp cir A | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04BC | 1212 | 2 | TEMP_SST_A | Saturated Suction Temp A | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04BE | 1214 | 2 | TEMP_SUCT_A | Compressor Suction Tmp A | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04C0 | 1216 | 2 | TEMP_ECO_T_A | EXV Eco. Tmp cir A | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04C2 | 1218 | 2 | TEMP_DGT_A | Discharge Gas Temp cir A | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04C4 | 1220 | 2 | TEMP_CP_TMP_A | Motor Temperature cir A | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04C6 | 1222 | 2 | EXV_CTRL_SH_A | Suction Superheat A | 32bits FLOAT | IR | ^F |  |  | 0
[7 empty] | ^C |  |  | 0
0x04C8 | 1224 | 2 | EXV_CTRL_DSH_A | Discharge Superheat A | 32bits FLOAT | IR | ^F |  |  | 0
[7 empty] | ^C |  |  | 0
0x04CA | 1226 | 2 | EXV_CTRL_pinch_a | Cooler ExchangeDT Cir A | 32bits FLOAT | IR | ^F |  |  | 0
[7 empty] | ^C |  |  | 0
0x04CC | 1228 | 2 | EXV_CTRL_EXV_A | EXV Position Circuit A | 32bits FLOAT | IR | PERCENT |  |  | 0
0x04CE | 1230 | 2 | OUTPUTS_VFAN_A | VariFan Speed A | 32bits FLOAT | IR | PERCENT |  |  | 0
0x04D0 | 1232 | 2 | FAN_CTRL_fan_f_a | Fan Freq Cir A | 32bits FLOAT | IR | HZ |  |  | 0
0x04D2 | 1234 | 2 | GENUNIT_CAPA_T | Cir A Total Capacity | 32bits FLOAT | IR | PERCENT |  |  | 0
0x04D4 | 1236 | 2 | CAPACTRL_overrida | Override Capacity A | 32bits UINT | IR |  |  |  | 0
0x04D6 | 1238 | 2 | ECO_CTRL_eco_a | EXV Eco Position Cir A | 32bits FLOAT | IR | PERCENT |  |  | 0
0x04D8 | 1240 | 2 | VLT_DRV_drv_pwra | Cir A Drive Power | 32bits FLOAT | IR | KW |  |  | 0
0x04DA | 1242 | 2 | VLT_DRV_drv_Ia | Cir A Drive Amps | 32bits FLOAT | IR | AMPS |  |  | 0
0x04DC | 1244 | 2 | VLT_DRV_drv_Va | Cir A Drive Voltage | 32bits FLOAT | IR | VOLTS |  |  | 0
0x04DE | 1246 | 2 | VLT_DRV_drv_Sa | Cir A Drive Speed | 32bits FLOAT | IR | RPM |  |  | 0
0x04E0 | 1248 | 2 | VLT_DRV_drv_Fa | Cir A Drive Frequency | 32bits FLOAT | IR | HZ |  |  | 0
0x04E2 | 1250 | 2 | FAN_DRV_fd_pwra1 | Fan Drive Power A1 | 32bits FLOAT | IR | KW |  |  | 0
0x04E4 | 1252 | 2 | FAN_DRV_fd_pwra2 | Fan Drive Power A2 | 32bits FLOAT | IR | KW |  |  | 0
0x04E6 | 1254 | 2 | FAN_DRV_fd_pwra3 | Fan Drive Power A3 | 32bits FLOAT | IR | KW |  |  | 0
0x04E8 | 1256 | 2 | INPUTS_OIL_L_A | Oil Level Input A | 32bits UINT | IR |  | 0 | 1 | 0
0x04F0 | 1264 | 2 | OUTPUTS_CP_A | Compressor A | 32bits UINT | IR |  | 0 | 1 | 0
0x0578 | 1400 | 2 | PRESSURE_DP_B | Discharge Pressure B | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x057A | 1402 | 2 | PRESSURE_SP_B | Main Suction Pressure B | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x057C | 1404 | 2 | PRESSURE_ECO_P_B | Economizer Pressure B | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x057E | 1406 | 2 | PRESSURE_OP_B | Oil Pressure B | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x0580 | 1408 | 2 | PRESSURE_DOP_B | Oil Pressure DifferenceB | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x0582 | 1410 | 2 | TEMP_SCT_B | Saturated Cond Tmp cir B | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0584 | 1412 | 2 | TEMP_SST_B | Saturated Suction Temp B | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0586 | 1414 | 2 | TEMP_SUCT_B | Compressor Suction Tmp B | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0588 | 1416 | 2 | TEMP_ECO_T_B | EXV Eco. Tmp cir B | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x058A | 1418 | 2 | TEMP_DGT_B | Discharge Gas Temp cir B | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x058C | 1420 | 2 | TEMP_CP_TMP_B | Motor Temperature cir B | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x058E | 1422 | 2 | EXV_CTRL_SH_B | Suction Superheat B | 32bits FLOAT | IR | ^F |  |  | 0
[7 empty] | ^C |  |  | 0
0x0590 | 1424 | 2 | EXV_CTRL_DSH_B | Discharge Superheat B | 32bits FLOAT | IR | ^F |  |  | 0
[7 empty] | ^C |  |  | 0
0x0592 | 1426 | 2 | EXV_CTRL_pinch_b | Cooler ExchangeDT Cir B | 32bits FLOAT | IR | ^F |  |  | 0
[7 empty] | ^C |  |  | 0
0x0594 | 1428 | 2 | EXV_CTRL_EXV_B | EXV Position Circuit B | 32bits FLOAT | IR | PERCENT |  |  | 0
0x0596 | 1430 | 2 | OUTPUTS_VFAN_B | VariFan Speed B | 32bits FLOAT | IR | PERCENT |  |  | 0
0x0598 | 1432 | 2 | FAN_CTRL_fan_f_b | Fan Freq Cir B | 32bits FLOAT | IR | HZ |  |  | 0
0x059A | 1434 | 2 | GENUNIT_CAPB_T | Cir B Total Capacity | 32bits FLOAT | IR | PERCENT |  |  | 0
0x059C | 1436 | 2 | CAPACTRL_overridb | Override Capacity B | 32bits UINT | IR |  |  |  | 0
0x059E | 1438 | 2 | ECO_CTRL_eco_b | EXV Eco Position Cir B | 32bits FLOAT | IR | PERCENT |  |  | 0
0x05A0 | 1440 | 2 | VLT_DRV_drv_pwrb | Cir B Drive Power | 32bits FLOAT | IR | KW |  |  | 0
0x05A2 | 1442 | 2 | VLT_DRV_drv_Ib | Cir B Drive Amps | 32bits FLOAT | IR | AMPS |  |  | 0
0x05A4 | 1444 | 2 | VLT_DRV_drv_Vb | Cir B Drive Voltage | 32bits FLOAT | IR | VOLTS |  |  | 0
0x05A6 | 1446 | 2 | VLT_DRV_drv_Sb | Cir B Drive Speed | 32bits FLOAT | IR | RPM |  |  | 0
0x05A8 | 1448 | 2 | VLT_DRV_drv_Fb | Cir B Drive Frequency | 32bits FLOAT | IR | HZ |  |  | 0
0x05AA | 1450 | 2 | FAN_DRV_fd_pwrb1 | Fan Drive Power B1 | 32bits FLOAT | IR | KW |  |  | 0
0x05AC | 1452 | 2 | FAN_DRV_fd_pwrb2 | Fan Drive Power B2 | 32bits FLOAT | IR | KW |  |  | 0
0x05AE | 1454 | 2 | FAN_DRV_fd_pwrb3 | Fan Drive Power B3 | 32bits FLOAT | IR | KW |  |  | 0
0x05B0 | 1456 | 2 | INPUTS_OIL_L_B | Oil Level Input B | 32bits UINT | IR |  | 0 | 1 | 0
0x05B8 | 1464 | 2 | OUTPUTS_CP_B | Compressor B | 32bits UINT | IR |  | 0 | 1 | 0
0x0708 | 1800 | 2 | RUNTIME_hr_cp_a1 | Compressor A1 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0710 | 1808 | 2 | RUNTIME_st_cp_a1 | Compressor A1 Starts | 32bits FLOAT | IR |  |  |  | 0
0x071A | 1818 | 2 | RUNTIME_hrfana01 | Circuit A Fan #1 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x071C | 1820 | 2 | RUNTIME_hrfana02 | Circuit A Fan #2 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x071E | 1822 | 2 | RUNTIME_hrfana03 | Circuit A Fan #3 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0720 | 1824 | 2 | RUNTIME_hrfana04 | Circuit A Fan #4 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0722 | 1826 | 2 | RUNTIME_hrfana05 | Circuit A Fan #5 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0724 | 1828 | 2 | RUNTIME_hrfana06 | Circuit A Fan #6 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0726 | 1830 | 2 | RUNTIME_hrfana07 | Circuit A Fan #7 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0728 | 1832 | 2 | RUNTIME_hrfana08 | Circuit A Fan #8 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x072A | 1834 | 2 | RUNTIME_hrfana09 | Circuit A Fan #9 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x072C | 1836 | 2 | RUNTIME_hrfana10 | Circuit A Fan #10 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x072E | 1838 | 2 | RUNTIME_hrfana11 | Circuit A Fan #11 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0730 | 1840 | 2 | RUNTIME_hrfana12 | Circuit A Fan #12 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0732 | 1842 | 2 | RUNTIME_hrfana13 | Circuit A Fan #13 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x0734 | 1844 | 2 | RUNTIME_hrfana14 | Circuit A Fan #14 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07D0 | 2000 | 2 | RUNTIME_hr_cp_b1 | Compressor B1 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07D8 | 2008 | 2 | RUNTIME_st_cp_b1 | Compressor B1 Starts | 32bits FLOAT | IR |  |  |  | 0
0x07E2 | 2018 | 2 | RUNTIME_hrfanb01 | Circuit B Fan #1 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07E4 | 2020 | 2 | RUNTIME_hrfanb02 | Circuit B Fan #2 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07E6 | 2022 | 2 | RUNTIME_hrfanb03 | Circuit B Fan #3 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07E8 | 2024 | 2 | RUNTIME_hrfanb04 | Circuit B Fan #4 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07EA | 2026 | 2 | RUNTIME_hrfanb05 | Circuit B Fan #5 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07EC | 2028 | 2 | RUNTIME_hrfanb06 | Circuit B Fan #6 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07EE | 2030 | 2 | RUNTIME_hrfanb07 | Circuit B Fan #7 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07F0 | 2032 | 2 | RUNTIME_hrfanb08 | Circuit B Fan #8 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07F2 | 2034 | 2 | RUNTIME_hrfanb09 | Circuit B Fan #9 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07F4 | 2036 | 2 | RUNTIME_hrfanb10 | Circuit B Fan #10 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07F6 | 2038 | 2 | RUNTIME_hrfanb11 | Circuit B Fan #11 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07F8 | 2040 | 2 | RUNTIME_hrfanb12 | Circuit B Fan #12 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07FA | 2042 | 2 | RUNTIME_hrfanb13 | Circuit B Fan #13 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x07FC | 2044 | 2 | RUNTIME_hrfanb14 | Circuit B Fan #14 Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x2328 | 9000 | 2 | FACTORY_unit_typ | Unit Type (Heatpump = 2) | 32bits UINT | IR |  | 1 | 2 | 1
0x232A | 9002 | 2 | FACTORY_unitsize | Unit Capacity | 32bits UINT | IR |  | 0 | 2000 | 0
0x232C | 9004 | 2 | FACTORY_mst_slv | Master Slave Selection | 32bits UINT | IR |  | 0 | 1 | 0
0x232E | 9006 | 2 | FACTORY_dcfc_sel | DC Free Cooling Select | 32bits UINT | IR |  | 0 | 1 | 0
0x2330 | 9008 | 2 | FACTORY_dxcooler | DX Cooler Select | 32bits UINT | IR |  | 0 | 1 | 0
0x2332 | 9010 | 2 | FACTORY_EC_Fan | EC Fan select | 32bits UINT | IR |  | 0 | 1 | 0
0x2334 | 9012 | 2 | FACTORY_emm_opt | Energy Management Module | 32bits UINT | IR |  | 0 | 1 | 0
0x2336 | 9014 | 2 | FACTORY_fan_ctrl | Fan Control Select | 32bits UINT | IR |  | 1 | 2 | 1
0x2338 | 9016 | 2 | FACTORY_heat_sel | Cooler Heater Select | 32bits UINT | IR |  | 0 | 2 | 0
0x233C | 9020 | 2 | FACTORY_opt_119 | Option 119 select | 32bits UINT | IR |  | 0 | 1 | 0
0x233E | 9022 | 2 | FACTORY_tier | Unit Tier | 32bits UINT | IR |  | 0 | 2 | 1
0x2340 | 9024 | 2 | FACTORY_varipump | VSPump option | 32bits UINT | IR |  | 0 | 2 | 0
0x2342 | 9026 | 2 | FACTORY_wtnk_htr | Water Tank Heater | 32bits UINT | IR |  | 0 | 1 | 0
0x2344 | 9028 | 2 | FACTORY_hfo | HFO refrigerant fluid | 32bits UINT | IR |  | 0 | 1 | 0
0x2346 | 9030 | 2 | FACTORY_highAmbt | High Ambient option | 32bits UINT | IR |  | 0 | 1 | 0
0x2348 | 9032 | 2 | FACTORY2_ClExchTp | Exchanger Type | 32bits UINT | IR |  |  |  | 0
0x234A | 9034 | 2 | FACTORY2_vfd_cmp | Nb VFD compressor | 32bits UINT | IR |  | 0 | 2 | 0
0x234C | 9036 | 2 | FACTORY2_vfd_fana | Nb Fan Drive cir A | 32bits UINT | IR |  | 0 | 3 | 0
0x234E | 9038 | 2 | FACTORY2_vfd_fanb | Nb Fan Drive cir B | 32bits UINT | IR |  | 0 | 3 | 0
0x2354 | 9044 | 2 | M_MSTSLV_cap_max | Max Available Capacity ? | 32bits UINT | IR |  | 0 | 1 | 0
0x2356 | 9046 | 2 | M_MSTSLV_l_strt_d | Lag Start Delay | 32bits UINT | IR | MINUTES |  |  | 0
0x2358 | 9048 | 2 | M_MSTSLV_lagstat | Slave lagstat | 32bits FLOAT | IR |  |  |  | 0
0x235A | 9050 | 2 | M_MSTSLV_lead_sel | Lead Unit is the: | 32bits UINT | IR |  | 0 | 1 | 0
0x235C | 9052 | 2 | M_MSTSLV_ll_chang | Lead/lag Changeover? | 32bits UINT | IR |  | 0 | 1 | 0
0x235E | 9054 | 2 | M_MSTSLV_ll_hr_d | Lead/lag Hours Delta | 32bits INT | IR | HOURS |  |  | 0
0x2360 | 9056 | 2 | M_MSTSLV_ll_pull | Lead Pulldown ? | 32bits UINT | IR |  | 0 | 1 | 0
0x2362 | 9058 | 2 | M_MSTSLV_ms_activ | Master/Slave Ctrl Active | 32bits UINT | IR |  | 0 | 1 | 0
0x2364 | 9060 | 2 | M_MSTSLV_ms_error | Master/Slave Error | 32bits INT | IR |  |  |  | 0
0x2366 | 9062 | 2 | M_MSTSLV_slav_ewt | Slave Cooler Ent. Fluid | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2368 | 9064 | 2 | M_MSTSLV_slav_hr | Slave Operating Hours | 32bits FLOAT | IR | HOURS |  |  | 0
0x236A | 9066 | 2 | M_MSTSLV_slav_lwt | Slave Cooler Leav. Fluid | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x236C | 9068 | 2 | M_MSTSLV_slv_capt | Slave Chiller Total Cap | 32bits UINT | IR | PERCENT |  |  | 0
0x236E | 9070 | 2 | M_MSTSLV_slv_stat | Slave Chiller State | 32bits UINT | IR |  |  |  | 0
0x2370 | 9072 | 2 | MST_SLV_lag_pump | Lag Unit Pump Control | 32bits UINT | IR |  | 0 | 1 | 0
0x2372 | 9074 | 2 | MST_SLV_lead_sel | Lead Lag Select | 32bits UINT | IR |  | 0 | 3 | 0
0x2374 | 9076 | 2 | MST_SLV_ll_serie | Chiller In Series | 32bits UINT | IR |  | 0 | 1 | 0
0x2376 | 9078 | 2 | MST_SLV_ms_ctrl | Master Control Type | 32bits UINT | IR |  | 1 | 3 | 1
0x2378 | 9080 | 2 | MST_SLV_ms_sel | Master/Slave Select | 32bits UINT | IR |  | 0 | 2 | 0
0x237A | 9082 | 2 | MST_SLV_slv_addr | Slave Address | 32bits UINT | IR |  | 1 | 236 | 2
0x237C | 9084 | 2 | PUMPSTAT_ROTCPUMP | Rotate Cooler Pumps ? | 32bits UINT | IR |  | 0 | 1 | 0
0x237E | 9086 | 2 | SETPOINT_cramp_sp | Cooling Ramp Loading | 32bits FLOAT | IR | ^F | 0.2 | 20 | 1
[7 empty] | ^C | 0.11111 | 11.1111 | 0.55556
0x2380 | 9088 | 2 | SETPOINT_hramp_sp | Heating Ramp Loading | 32bits FLOAT | IR | ^F | 0.2 | 20 | 1
[7 empty] | ^C | 0.11111 | 11.1111 | 0.55556
0x2382 | 9090 | 2 | SETPOINT_cauto_sp | Cool Changeover Setpt | 32bits FLOAT | IR | °F | 39 | 122 | 75
[7 empty] | °C | 3.8889 | 50 | 23.8889
0x2384 | 9092 | 2 | SETPOINT_hauto_sp | Heat Changeover Setpt | 32bits FLOAT | IR | °F | 32 | 115 | 64
[7 empty] | °C | 1.2e-06 | 46.1111 | 17.7778
0x2386 | 9094 | 2 | SETPOINT_vpmpdtsp | Varipump Delta Temp Stp | 32bits FLOAT | IR | ^F | 1.8 | 36 | 9
[7 empty] | ^C | 1 | 20 | 5
0x2388 | 9096 | 2 | SETPOINT_vpmpdpsp | Varipump Pressure Stp | 32bits FLOAT | IR | PSIG | 7.25 | 90 | 29
[7 empty] | kPa | 49.9887 | 620.55 | 199.955
0x238A | 9098 | 2 | RECLAIM_RECL_SEL | Reclaim Selection | 32bits UINT | IR |  | 0 | 1 | 0
0x238C | 9100 | 2 | RECLAIM_HR_stat | Reclaim Status | 32bits UINT | IR |  | 0 | 1 | 0
0x238E | 9102 | 2 | RECLAIM_HRCtrPnt | Reclaim control point | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2390 | 9104 | 2 | RECLAIM_HRCtrWat | Reclaim controlled water | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2392 | 9106 | 2 | RECLAIM_HR_FLOW | Heat Reclaim Flow switch | 32bits UINT | IR |  |  |  | 0
0x2394 | 9108 | 2 | RECLAIM_HR_EWT | HR Entering Fluid temp | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2396 | 9110 | 2 | RECLAIM_HR_LWT | HR Leaving Fluid temp | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2398 | 9112 | 2 | RECLAIM_HEATER_A | Reclaim BPHE Heater A | 32bits UINT | IR |  | 0 | 1 | 0
0x239A | 9114 | 2 | RECLAIM_HEATER_B | Reclaim BPHE Heater B | 32bits UINT | IR |  | 0 | 1 | 0
0x239C | 9116 | 2 | RECLAIM_HRWTR_VA | Reclaim water valve A | 32bits UINT | IR |  | 0 | 1 | 0
0x239E | 9118 | 2 | RECLAIM_HRWTR_VB | Reclaim water valve B | 32bits UINT | IR |  | 0 | 1 | 0
0x23A0 | 9120 | 2 | RECLAIM_HR_3WV | Reclaim 3Way Valve cmd | 32bits FLOAT | IR | PERCENT | 0 | 100 | 0
0x23A2 | 9122 | 2 | RECLAIM_HR3WVout | Reclaim 3Way Valve outp | 32bits FLOAT | IR | VOLTS | 0 | 10 | 0
0x23A4 | 9124 | 2 | RECLAIM_HR3WVmod | Reclaim 3Way Valve mode | 32bits UINT | IR |  | 0 | 1 | 0
0x23A6 | 9126 | 2 | RECLAIM_act_3WV | Reclaim 3WV activated | 32bits UINT | IR |  | 0 | 1 | 1
0x23A8 | 9128 | 2 | RECLAIM_HR_PMP | Reclaim pump command | 32bits UINT | IR |  | 0 | 1 | 0
0x23AA | 9130 | 2 | RECLAIM_HR_X_enA | Reclaim EXV A enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23AC | 9132 | 2 | RECLAIM_HR_X_enB | Reclaim EXV B enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23AE | 9134 | 2 | RECLAIM_HR_F_enA | Reclaim Fan A enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23B0 | 9136 | 2 | RECLAIM_HR_F_enB | Reclaim Fan B enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23B2 | 9138 | 2 | RECLAIM_HR_E_enA | Reclaim Eco A enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23B4 | 9140 | 2 | RECLAIM_HR_E_enB | Reclaim Eco B enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23B6 | 9142 | 2 | RECLAIM_HR_C_enA | Reclaim Cmp A enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23B8 | 9144 | 2 | RECLAIM_HR_C_enB | Reclaim Cmp B enabled | 32bits UINT | IR |  | 0 | 1 | 0
0x23BA | 9146 | 2 | RECLAIM_HR_3WVen | Reclaim 3Way Valv enable | 32bits UINT | IR |  | 0 | 1 | 0
0x23BC | 9148 | 2 | HR_CFG_hr_cir | HR circuit selection | 32bits UINT | IR |  | 0 | 2 | 2
0x23BE | 9150 | 2 | HR_CFG_hr_flui | HR condenser fluid | 32bits UINT | IR |  | 0 | 1 | 0
0x23C0 | 9152 | 2 | HR_CFG_hr_eco | HR eco mode | 32bits UINT | IR |  | 0 | 1 | 0
0x23C2 | 9154 | 2 | HR_CFG_rev_3WV | HR reverse 3WV cmd ? | 32bits UINT | IR |  | 0 | 1 | 0
0x23C4 | 9156 | 2 | HR_CFG_HRewtctl | HR Control on EWT | 32bits UINT | IR |  | 0 | 1 | 0
0x23C6 | 9158 | 2 | HR_CFG_pg_HR3wv | Prop PID gain HR 3w valv | 32bits FLOAT | IR |  | -20 | 20 | 2
0x23C8 | 9160 | 2 | HR_CFG_ig_HR3wv | Int PID gain HR 3w valve | 32bits FLOAT | IR |  | -5 | 5 | 0.2
0x23CA | 9162 | 2 | HR_CFG_dg_HR3wv | Deri PID gain HR 3w valv | 32bits FLOAT | IR |  | -20 | 20 | 0.4
0x23CC | 9164 | 2 | GENCONF_minHR3wv | HR 3w valve min position | 32bits FLOAT | IR | PERCENT | 0 | 100 | 20
0x23CE | 9166 | 2 | GENCONF_maxHR3wv | HR 3w valve max position | 32bits FLOAT | IR | PERCENT | 0 | 100 | 80
0x23D0 | 9168 | 2 | SETPOINT_rsp | Heat Reclaim Setpoint | 32bits FLOAT | IR | °F | 68 | 149 | 122
[7 empty] | °C | 20 | 65 | 50
0x23D6 | 9174 | 2 | ENERGY_coolPowA | Cooling Power A | 32bits FLOAT | IR | KW |  |  | 0
0x23D8 | 9176 | 2 | ENERGY_coolPowB | Cooling Power B | 32bits FLOAT | IR | KW |  |  | 0
0x23DA | 9178 | 2 | ENERGY_coolPowT | Cooling Power Total | 32bits FLOAT | IR | KW |  |  | 0
0x23DC | 9180 | 2 | ENERGY_eerA | Energy Efficiency A | 32bits FLOAT | IR |  |  |  | 0
0x23DE | 9182 | 2 | ENERGY_eerB | Energy Efficiency B | 32bits FLOAT | IR |  |  |  | 0
0x23E0 | 9184 | 2 | ENERGY_eer | Energy Efficiency | 32bits FLOAT | IR |  |  |  | 0
0x23E2 | 9186 | 2 | ENERGY_powIn | Electrical Power input | 32bits FLOAT | IR | KW |  |  | 0
0x23E4 | 9188 | 2 | ENERGY_powPmp | Pump Elec Power Input | 32bits FLOAT | IR | KW |  |  | 0
0x23E6 | 9190 | 2 | ENERGY_cPowT_m2 | Cooling Power Total | 32bits FLOAT | IR | KW |  |  | 0
0x23E8 | 9192 | 2 | ENERGY_eerA_m2 | Energy Efficiency A | 32bits FLOAT | IR |  |  |  | 0
0x23EA | 9194 | 2 | ENERGY_eerB_m2 | Energy Efficiency B | 32bits FLOAT | IR |  |  |  | 0
0x23EC | 9196 | 2 | ENERGY_eer_m2 | Energy Efficiency | 32bits FLOAT | IR |  |  |  | 0
0x23EE | 9198 | 2 | ENERGY_energyIn | Electrical Energy input | 32bits FLOAT | IR | KWH |  |  | 0
0x23F0 | 9200 | 2 | ENERGY_energyP | Pump Elec Energy Input | 32bits FLOAT | IR | KWH |  |  | 0
0x23F2 | 9202 | 2 | ENERGY_energOut | Cooling Energy output | 32bits FLOAT | IR | KWH |  |  | 0
0x23F4 | 9204 | 2 | ENERGY_energEER | Integrated EER | 32bits FLOAT | IR |  |  |  | 0
0x23F6 | 9206 | 2 | ENERGY_reset_da | Last Reset Date | 32bits FLOAT | IR |  |  |  | 0
0x23F8 | 9208 | 2 | ENERGY_reset_ti | Last Reset time | 32bits UINT | IR |  |  |  | 0
0x23FA | 9210 | 2 | ENERGY_pmp_date | Pump Last Reset Date | 32bits FLOAT | IR |  |  |  | 0
0x23FC | 9212 | 2 | ENERGY_pmp_time | Pump Last Reset time | 32bits UINT | IR |  |  |  | 0
0x23FE | 9214 | 2 | ENERGY_cPowA_m2 | Cooling Power A | 32bits FLOAT | IR | KW |  |  | 0
0x2400 | 9216 | 2 | ENERGY_cPowB_m2 | Cooling Power B | 32bits FLOAT | IR | KW |  |  | 0
0x2402 | 9218 | 2 | ENGMETER_p_total | Total active power | 32bits FLOAT | IR | KW |  |  | 0
0x2404 | 9220 | 2 | ENGMETER_e_total | Total input energy | 32bits FLOAT | IR | KWH |  |  | 0
0x2406 | 9222 | 2 | ENGMETER_e_reset | Input energy since reset | 32bits FLOAT | IR | KWH |  |  | 0
0x2408 | 9224 | 2 | ENGMETER_e_start | Input energy since start | 32bits FLOAT | IR | KWH |  |  | 0
0x240A | 9226 | 2 | ENGMETER_p_max | Max active power | 32bits FLOAT | IR | KW |  |  | 0
0x240C | 9228 | 2 | ENGMETER_I1 | Single phase current | 32bits FLOAT | IR | AMPS |  |  | 0
0x240E | 9230 | 2 | ENGMETER_THD | Total harmonic distortn | 32bits FLOAT | IR | PERCENT |  |  | 0
0x2410 | 9232 | 2 | ENGMETER_FP | Power factor | 32bits FLOAT | IR |  |  |  | 0
0x2412 | 9234 | 2 | ENGMETER_p_tota2 | Total active power 2 | 32bits FLOAT | IR | KW |  |  | 0
0x2414 | 9236 | 2 | ENGMETER_e_tota2 | Total input energy 2 | 32bits FLOAT | IR | KWH |  |  | 0
0x2416 | 9238 | 2 | ENGMETER_e_rese2 | Input energy since rst2 | 32bits FLOAT | IR | KWH |  |  | 0
0x2418 | 9240 | 2 | ENGMETER_e_star2 | Input energy since strt2 | 32bits FLOAT | IR | KWH |  |  | 0
0x241A | 9242 | 2 | ENGMETER_p_max2 | Max active power 2 | 32bits FLOAT | IR | KW |  |  | 0
0x241C | 9244 | 2 | ENGMETER_I1_2 | Single phase current 2 | 32bits FLOAT | IR | AMPS |  |  | 0
0x241E | 9246 | 2 | ENGMETER_THD2 | Total harmonic distrtn2 | 32bits FLOAT | IR | PERCENT |  |  | 0
0x2420 | 9248 | 2 | ENGMETER_FP2 | Power factor 2 | 32bits FLOAT | IR |  |  |  | 0

## Variables Modbus elegidas
Address |  | Reg. N° | Parameter | Description | Display Mode | Type | Unit | Value |  |  | Comment
hexadecimal | decimal | [6 empty] | Min. | Max. | Default
0x0001 | 1 | 1 | ALM_COOLER_FREEZE_F | Cooler Freeze Protection | 1bit BOOL | DI |  | 0 | 1 | 0
0x0384 | 900 | 2 | SETPOINT_csp1 | Cooling Setpoint 1 | 32bits FLOAT | HR | °F | -20 | 78.8 | 44
[7 empty] | °C | -28.8889 | 26 | 6.6667
0x0386 | 902 | 2 | SETPOINT_csp2 | Cooling Setpoint 2 | 32bits FLOAT | HR | °F | -20 | 78.8 | 44
[7 empty] | °C | -28.8889 | 26 | 6.6667
0x0388 | 904 | 2 | SETPOINT_ice_sp | Cooling Ice Setpoint | 32bits FLOAT | HR | °F | -20 | 78.8 | 44
[7 empty] | °C | -28.8889 | 26 | 6.6667
0x038A | 906 | 2 | SETPOINT_hsp1 | Heating Setpoint 1 | 32bits FLOAT | HR | °F | 80 | 145.4 | 100
[7 empty] | °C | 26.6667 | 63 | 37.7778
0x038C | 908 | 2 | SETPOINT_hsp2 | Heating Setpoint 2 | 32bits FLOAT | HR | °F | 80 | 145.4 | 100
[7 empty] | °C | 26.6667 | 63 | 37.7778
0x038E | 910 | 2 | SETPOINT_lim_sp1 | Switch Limit Setpoint 1 | 32bits UINT | HR | PERCENT | 0 | 100 | 100
0x0390 | 912 | 2 | SETPOINT_lim_sp2 | Switch Limit Setpoint 2 | 32bits UINT | HR | PERCENT | 0 | 100 | 100
0x0392 | 914 | 2 | SETPOINT_lim_sp3 | Switch Limit Setpoint 3 | 32bits UINT | HR | PERCENT | 0 | 100 | 100
0x0BC2 | 3010 | 2 | PROTOCOL_CTRL_PNT | Control Point | 32bits FLOAT | HR | °F | -4 | 153 | 44.6
[7 empty] | °C | -20 | 67.2222 | 7
0x0BC6 | 3014 | 2 | PROTOCOL_DEM_LIM | Demand Limit | 32bits UINT | HR | PERCENT | 0 | 100 | 0
0x0BCE | 3022 | 2 | PROTOCOL_CHIL_S_S | Chiller Start/Stop | 32bits UINT | HR |  | 0 | 1 | 0
0x0BD0 | 3024 | 2 | PROTOCOL_EMSTOP | Emergency Stop | 32bits UINT | HR |  | 0 | 1 | 0
0x1004 | 4100 | 2 | GENCONF_ice_cnfg | Ice Mode Enable | 32bits UINT | HR |  | 0 | 1 | 0
0x1016 | 4118 | 2 | GENCONF_pow_max | Maximum Power Limit | 32bits FLOAT | HR | KW | 0 | 2000 | 2000
0x1018 | 4120 | 2 | GENCONF_pow_sel | Power Limit select | 32bits UINT | HR |  | 0 | 1 | 0
0x0004 | 4 | 2 | TEMP_OAT | Outdoor Air Temperature | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0006 | 6 | 2 | CAPACTRL_ctrl_wt | Controled Water Temp | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0008 | 8 | 2 | TEMP_CHWSTEMP | CHWS Temperature | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x000A | 10 | 2 | GENUNIT_CTRL_PNT | Control Point | 32bits FLOAT | IR | °F | -4 | 153 | 0
[7 empty] | °C | -20 | 67.2222 | -17.7778
0x000C | 12 | 2 | GENUNIT_SP | Current Setpoint | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0016 | 22 | 2 | GENUNIT_CHIL_S_S | Net.: Cmd Start/Stop | 32bits UINT | IR |  | 0 | 1 | 0
0x0018 | 24 | 2 | GENUNIT_EMSTOP | Emergency Stop | 32bits UINT | IR |  | 0 | 1 | 0
0x002A | 42 | 2 | UNIT_STATUS | Run Status | 32bits UINT | IR |  |  |  | 0
0x0048 | 72 | 2 | PRESSURE_EWATPRES | Entering water pressure | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x004A | 74 | 2 | PRESSURE_LWATPRES | Leaving water pressure | 32bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x044C | 1100 | 2 | ALARMRST_alarm_1c | Current Alarm 1 | 32bits UINT | IR |  |  |  | 0
0x0460 | 1120 | 2 | UNIT_ALM | Alarm Status | 32bits UINT | IR |  |  |  | 0
0x2394 | 9108 | 2 | RECLAIM_HR_EWT | HR Entering Fluid temp | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2396 | 9110 | 2 | RECLAIM_HR_LWT | HR Leaving Fluid temp | 32bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778